- TMV -6 – Thermostatic mixing valve (factory set to 85°F) for single emergency eye or eye/face wash and shower safety station. Unit shall include a built-in cold water bypass, rough bronze finish, solid bimetal thermostat, locking temperature regulator with high temperature limit stop factory set for 90°F, integral check stops, and dial thermometer. Unit shall be mounted in a recessed 16 gauge type 304 stainless steel cabinet with #4 brushed satin finish, with door and lock.

- Performance:  Unit shall have a flow range of 3 GPM to 38 GPM with a maximum pressure loss of 30 PSI and come with a full 2-year warranty.

- Quality Assurance: Unit shall be certified to ASSE 1071. Unit shall be certified to meet Low Lead requirements of wetted surface area containing less than 0.25% lead by weight.

- Fixture:  Guardian G3807LF