- TMV - 8 – Thermostatic mixing valve (factory set to 85°F) for multiple emergency eyewash and shower units. Unit shall include a built-in cold water bypass, rough bronze finish, solid bimetal thermostat, locking temperature regulator with high temperature limit stop factory set for 90°F, integral check stops, and dial thermometer.

- Performance:  Unit shall have a flow range of 3 GPM to 99 GPM with a maximum pressure loss of 30 PSI and comes with a full 2-year warranty.

- Quality Assurance: Unit shall be certified to meet Low Lead requirements of wetted surface area containing less than 0.25% lead by weight.

- Fixture:  Guardian G3900LF