WATER TEMPERING EQUIPMENT

- MANUFACTURER

  - Guardian Equipment

- Tempering Skid

- Description: Factory assembled and tested skid-mounted tempering system capable of supplying an uninterrupted flow of tepid water to emergency eyewashes and safety showers at a rate of 23 GPM for 15 minutes.

- Skid-mounted, packaged water tempering unit shall incorporate the following main components:

  - Heavy Duty Galvanized Steel Base with Fork Lift Slots

  - Schedule 40, Galvanized Piping

  - Insulated Water Tank with 9 Kw Heater

  - Expansion Tank

  - Inline Recirculation Heater with High Temperature Shut-Off

  - Inline Ultraviolet Water Purifier

  - UL-Listed Fused Control Panel

  - Thermostatic Mixing Valve with Temperature Override (3 GPM-23 GPM)

  - Recirculation Pump with Reverse Action Pressure Switch

- Skid to be factory assembled, wired, tested and incorporate all the necessary hydraulic and electrical components for operation.

  - Skid to be wired for single point power connection

  - UL-Listed Control Panel

  - Skid to be piped for three hydraulic points of connection:

    - Domestic Cold Water Supply Inlet

    - Recirculation Loop Inlet

    - Recirculation Loop Outlet

- Basis of Design:  Guardian Equipment Model G4110